#### 1. GENERAL DATA AND INFORMATION:

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Bay No. |  |  | Designation |  |
| Bay Name |  |  | Order No. |  |
| Manufacturer  | AREVA |  | Serial no. |  |
| Dwg & Sh No. |  |  | Aux. Voltage | 110 - 125 VDC |
| Flag Type | Electrical Reset |  | No. of Contacts |  NO + NC |

#### 2. MECHANICAL CHECKS AND VISUAL INSPECTION:

|  |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | CHECKED |
| 1 | Inspect for any physical damage or defects. |  |
| 2 | Verify nameplate information for correctness |  |
| 3 | Check tightness of all bolted connections. |  |
| 4 | Check all grounding connections are securely fix |  |
| 5 | Verify connections as per approved drawing |  |
| 6 | Check reset operation |  |

#### 3. ELECTRICAL TESTS:

###### A. FUNCTION TEST:

|  |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | CHECKED |
| 1 | All contact checked |  |
| 2 | All output contacts resistance checked |  |
| 3 | Flag Operation Checked |  |

###### B. PICKUP / DROP OFF VOLTAGE TEST:

|  |  |
| --- | --- |
| **Pick Up** | **Drop Off** |
| **Volts (V)** | **Current (mA)** | **Volts (V)** | **Current (mA)** |
|  |  |  |  |
|  |  |  |  |

 Operating Range :

Minimum Operating Voltage 35% of lower rated voltage ( As per technical data )

###### C. PICKUP / DROP OFF TIMING TEST : (AS RATED VOLTAGE)

|  |  |  |  |
| --- | --- | --- | --- |
| **Pick Up (ms)** | **Contact** **Terminals** | **Drop Off (ms)** | **Contact** **Terminals** |
|  |  |  |  |
|  |  |  |  |

 **Limits** **:**

Pick up Time < 8 ms , Drop off time < 15 ms ( As per technical data )

###### D. RELAY BURDEN TEST:

|  |  |  |
| --- | --- | --- |
| **Voltage (V)** | **Current (mA)** | **Relay Burden** **Watts (W)** |
| 125 |  |  |

 **Limits :** Relay Burden ≤ 4 W ( As per technical data )