## RET 670 Diff Pickup
| RET 670 Transformer Differential 1/3-Phase Pickup calculation | [7 empty] | ABB
NEW RAFHA PP S/S DATE : 01/07/2012
|  |  | FINAL TEST |  |  | CIRCUIT No : UAT3
POSN | WDG | With Zero Seq =ON | With Zero Seq =OFF |  | Id min = | 40 |  |  |  | Dy01d00
0 | Reference | 0.66667 | 1 |  | Trafo connection |  |  | W1 ZCOM |  | 181
1 | 30 deg lag | 0.57735 | 0.57735 | [6 empty] | 2
2 | 60 deg lag | 0.33333 | -1 | 240 deg. phase shift |  |  |  | W2 ZCOM |  | 1
3 | 90 deg lag | -0.58 | -0.58 | 240 deg. phase shift
4 | 120 deg lag | -0.33333 | 1 | 120 deg. phase shift | [5 empty] | 2
5 | 150 deg lag | -0.57735 | -0.57735
6 | 180 deg | -0.66667 | -1 |  |  |  | Primary | Sec.
7 | 150 deg lead | -0.57735 | -0.57735 |  |  | W1 | 800 | 1
8 | 120 deg lead | -0.33333 | 1 | 240 deg. phase shift |  | W2 | 2000 | 1
9 | 90 deg lead | 0.58 | 0.58 | 240 deg. phase shift
10 | 60 deg lead | 0.33333 | -1 | 120 deg. phase shift
11 | 30 deg lead | 0.57735 | 0.57735
WDG | Relative Clock | VOLT (KV) | MVA | CURRENT (A) | CTR | BASE WRT W1 | Z comp | Pick up 1-Ph | MF
W1 | 11 | 132 | 100 | 437.3866 | 800 | 437.3866 | OFF | 0.37879 | 0.57735
W2 | 00 | 33 | 100 | 1749.5463 | 2000 | 1749.5463 | ON | 0.52486 | 0.66667
11
Note :
2) Current Base reference is W1 rated current
|  | With Zero Seq =ON |  |  | With Zero Seq =OFF
|  | 0 | 0.66667 |  | 0 | 1
|  | 1 | 0.57735 |  | 1 | 0.57735
|  | 2 | 0.33333 |  | 2 | -1
|  | 3 | -0.58 |  | 3 | -0.58
|  | 4 | -0.33333 |  | 4 | 1
|  | 5 | -0.57735 |  | 5 | -0.57735
|  | 6 | -0.66667 |  | 6 | -1
|  | 7 | -0.57735 |  | 7 | -0.57735
|  | 8 | -0.33333 |  | 8 | 1
|  | 9 | 0.58 |  | 9 | 0.58
|  | 10 | 0.33333 |  | 10 | -1
|  | 11 | 0.57735 |  | 11 | 0.57735
WDG | Relative Clock | VOLT (KV) | MVA | CURRENT (A) | CTR | BASE WRT W1 | Z comp | Pick up 3-Ph | MF
W1 | 11 | 132 | 100 | 437.3866 | 800 | 437.3866 | OFF | 0.21869 | 1
W2 | 00 | 33 | 100 | 1749.5463 | 2000 | 1749.5463 | ON | 0.34991 | 1
ENTER YOUR VALUES IN CELLS MARKED WITH THIS YELLOW COLOR

## Trafo combinations
[7 empty] | First Y is reference |  |  | First Y is reference |  |  | First Y is reference revised
W1 | W2 | W3 | W1 | W2 | W3 |  | W1 | W2 | W3 | W1 | W2 | W3 | W1 | W2 | W3
Y | y | y | 00 | 00 | 00 | Yy00y00 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 00
Y | y | y | 00 | 00 | 02 | Yy00y02 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 02
Y | y | y | 00 | 00 | 04 | Yy00y04 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 04
Y | y | y | 00 | 00 | 06 | Yy00y06 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 06
Y | y | y | 00 | 00 | 08 | Yy00y08 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 08
Y | y | y | 00 | 00 | 10 | Yy00y10 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 10
Y | y | y | 00 | 02 | 00 | Yy02y00 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 00
Y | y | y | 00 | 02 | 02 | Yy02y02 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 02
Y | y | y | 00 | 02 | 04 | Yy02y04 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 04
Y | y | y | 00 | 02 | 06 | Yy02y06 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 06
Y | y | y | 00 | 02 | 08 | Yy02y08 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 08
Y | y | y | 00 | 02 | 10 | Yy02y10 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 10
Y | y | y | 00 | 04 | 00 | Yy04y00 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 00
Y | y | y | 00 | 04 | 02 | Yy04y02 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 02
Y | y | y | 00 | 04 | 04 | Yy04y04 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 04
Y | y | y | 00 | 04 | 06 | Yy04y06 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 06
Y | y | y | 00 | 04 | 08 | Yy04y08 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 08
Y | y | y | 00 | 04 | 10 | Yy04y10 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 10
Y | y | y | 00 | 06 | 00 | Yy06y00 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 00
Y | y | y | 00 | 06 | 02 | Yy06y02 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 02
Y | y | y | 00 | 06 | 04 | Yy06y04 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 04
Y | y | y | 00 | 06 | 06 | Yy06y06 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 06
Y | y | y | 00 | 06 | 08 | Yy06y08 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 08
Y | y | y | 00 | 06 | 10 | Yy06y10 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 10
Y | y | y | 00 | 08 | 00 | Yy08y00 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 00
Y | y | y | 00 | 08 | 02 | Yy08y02 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 02
Y | y | y | 00 | 08 | 04 | Yy08y04 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 04
Y | y | y | 00 | 08 | 06 | Yy08y06 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 06
Y | y | y | 00 | 08 | 08 | Yy08y08 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 08
Y | y | y | 00 | 08 | 10 | Yy08y10 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 10
Y | y | y | 00 | 10 | 00 | Yy10y00 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 00
Y | y | y | 00 | 10 | 02 | Yy10y02 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 02
Y | y | y | 00 | 10 | 04 | Yy10y04 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 04
Y | y | y | 00 | 10 | 06 | Yy10y06 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 06
Y | y | y | 00 | 10 | 08 | Yy10y08 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 08
Y | y | y | 00 | 10 | 10 | Yy10y10 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 10
Y | y | d | 00 | 00 | 01 | Yy00d01 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 01
Y | y | d | 00 | 00 | 03 | Yy00d03 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 03
Y | y | d | 00 | 00 | 05 | Yy00d05 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 05
Y | y | d | 00 | 00 | 07 | Yy00d07 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 07
Y | y | d | 00 | 00 | 09 | Yy00d09 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 09
Y | y | d | 00 | 00 | 11 | Yy00d11 | First Y is reference W1: 00; First Y is reference W2: 00; First Y is reference W3: 11
Y | y | d | 00 | 02 | 01 | Yy02d01 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 01
Y | y | d | 00 | 02 | 03 | Yy02d03 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 03
Y | y | d | 00 | 02 | 05 | Yy02d05 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 05
Y | y | d | 00 | 02 | 07 | Yy02d07 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 07
Y | y | d | 00 | 02 | 09 | Yy02d09 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 09
Y | y | d | 00 | 02 | 11 | Yy02d11 | First Y is reference W1: 00; First Y is reference W2: 02; First Y is reference W3: 11
Y | y | d | 00 | 04 | 01 | Yy04d01 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 01
Y | y | d | 00 | 04 | 03 | Yy04d03 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 03
Y | y | d | 00 | 04 | 05 | Yy04d05 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 05
Y | y | d | 00 | 04 | 07 | Yy04d07 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 07
Y | y | d | 00 | 04 | 09 | Yy04d09 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 09
Y | y | d | 00 | 04 | 11 | Yy04d11 | First Y is reference W1: 00; First Y is reference W2: 04; First Y is reference W3: 11
Y | y | d | 00 | 06 | 01 | Yy06d01 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 01
Y | y | d | 00 | 06 | 03 | Yy06d03 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 03
Y | y | d | 00 | 06 | 05 | Yy06d05 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 05
Y | y | d | 00 | 06 | 07 | Yy06d07 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 07
Y | y | d | 00 | 06 | 09 | Yy06d09 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 09
Y | y | d | 00 | 06 | 11 | Yy06d11 | First Y is reference W1: 00; First Y is reference W2: 06; First Y is reference W3: 11
Y | y | d | 00 | 08 | 01 | Yy08d01 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 01
Y | y | d | 00 | 08 | 03 | Yy08d03 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 03
Y | y | d | 00 | 08 | 05 | Yy08d05 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 05
Y | y | d | 00 | 08 | 07 | Yy08d07 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 07
Y | y | d | 00 | 08 | 09 | Yy08d09 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 09
Y | y | d | 00 | 08 | 11 | Yy08d11 | First Y is reference W1: 00; First Y is reference W2: 08; First Y is reference W3: 11
Y | y | d | 00 | 10 | 01 | Yy10d01 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 01
Y | y | d | 00 | 10 | 03 | Yy10d03 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 03
Y | y | d | 00 | 10 | 05 | Yy10d05 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 05
Y | y | d | 00 | 10 | 07 | Yy10d07 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 07
Y | y | d | 00 | 10 | 09 | Yy10d09 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 09
Y | y | d | 00 | 10 | 11 | Yy10d11 | First Y is reference W1: 00; First Y is reference W2: 10; First Y is reference W3: 11
Y | d | y | 00 | 01 | 00 | Yd01y00 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 00
Y | d | y | 00 | 01 | 02 | Yd01y02 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 02
Y | d | y | 00 | 01 | 04 | Yd01y04 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 04
Y | d | y | 00 | 01 | 06 | Yd01y06 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 06
Y | d | y | 00 | 01 | 08 | Yd01y08 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 08
Y | d | y | 00 | 01 | 10 | Yd01y10 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 10
Y | d | y | 00 | 03 | 00 | Yd03y00 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 00
Y | d | y | 00 | 03 | 02 | Yd03y02 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 02
Y | d | y | 00 | 03 | 04 | Yd03y04 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 04
Y | d | y | 00 | 03 | 06 | Yd03y06 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 06
Y | d | y | 00 | 03 | 08 | Yd03y08 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 08
Y | d | y | 00 | 03 | 10 | Yd03y10 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 10
Y | d | y | 00 | 05 | 00 | Yd05y00 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 00
Y | d | y | 00 | 05 | 02 | Yd05y02 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 02
Y | d | y | 00 | 05 | 04 | Yd05y04 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 04
Y | d | y | 00 | 05 | 06 | Yd05y06 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 06
Y | d | y | 00 | 05 | 08 | Yd05y08 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 08
Y | d | y | 00 | 05 | 10 | Yd05y10 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 10
Y | d | y | 00 | 07 | 00 | Yd07y00 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 00
Y | d | y | 00 | 07 | 02 | Yd07y02 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 02
Y | d | y | 00 | 07 | 04 | Yd07y04 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 04
Y | d | y | 00 | 07 | 06 | Yd07y06 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 06
Y | d | y | 00 | 07 | 08 | Yd07y08 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 08
Y | d | y | 00 | 07 | 10 | Yd07y10 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 10
Y | d | y | 00 | 09 | 00 | Yd09y00 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 00
Y | d | y | 00 | 09 | 02 | Yd09y02 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 02
Y | d | y | 00 | 09 | 04 | Yd09y04 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 04
Y | d | y | 00 | 09 | 06 | Yd09y06 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 06
Y | d | y | 00 | 09 | 08 | Yd09y08 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 08
Y | d | y | 00 | 09 | 10 | Yd09y10 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 10
Y | d | y | 00 | 11 | 00 | Yd11y00 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 00
Y | d | y | 00 | 11 | 02 | Yd11y02 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 02
Y | d | y | 00 | 11 | 04 | Yd11y04 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 04
Y | d | y | 00 | 11 | 06 | Yd11y06 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 06
Y | d | y | 00 | 11 | 08 | Yd11y08 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 08
Y | d | y | 00 | 11 | 10 | Yd11y10 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 10
Y | d | d | 00 | 01 | 01 | Yd01d01 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 01
Y | d | d | 00 | 01 | 03 | Yd01d03 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 03
Y | d | d | 00 | 01 | 05 | Yd01d05 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 05
Y | d | d | 00 | 01 | 07 | Yd01d07 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 07
Y | d | d | 00 | 01 | 09 | Yd01d09 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 09
Y | d | d | 00 | 01 | 11 | Yd01d11 | First Y is reference W1: 00; First Y is reference W2: 01; First Y is reference W3: 11
Y | d | d | 00 | 03 | 01 | Yd03d01 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 01
Y | d | d | 00 | 03 | 03 | Yd03d03 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 03
Y | d | d | 00 | 03 | 05 | Yd03d05 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 05
Y | d | d | 00 | 03 | 07 | Yd03d07 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 07
Y | d | d | 00 | 03 | 09 | Yd03d09 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 09
Y | d | d | 00 | 03 | 11 | Yd03d11 | First Y is reference W1: 00; First Y is reference W2: 03; First Y is reference W3: 11
Y | d | d | 00 | 05 | 01 | Yd05d01 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 01
Y | d | d | 00 | 05 | 03 | Yd05d03 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 03
Y | d | d | 00 | 05 | 05 | Yd05d05 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 05
Y | d | d | 00 | 05 | 07 | Yd05d07 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 07
Y | d | d | 00 | 05 | 09 | Yd05d09 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 09
Y | d | d | 00 | 05 | 11 | Yd05d11 | First Y is reference W1: 00; First Y is reference W2: 05; First Y is reference W3: 11
Y | d | d | 00 | 07 | 01 | Yd07d01 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 01
Y | d | d | 00 | 07 | 03 | Yd07d03 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 03
Y | d | d | 00 | 07 | 05 | Yd07d05 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 05
Y | d | d | 00 | 07 | 07 | Yd07d07 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 07
Y | d | d | 00 | 07 | 09 | Yd07d09 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 09
Y | d | d | 00 | 07 | 11 | Yd07d11 | First Y is reference W1: 00; First Y is reference W2: 07; First Y is reference W3: 11
Y | d | d | 00 | 09 | 01 | Yd09d01 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 01
Y | d | d | 00 | 09 | 03 | Yd09d03 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 03
Y | d | d | 00 | 09 | 05 | Yd09d05 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 05
Y | d | d | 00 | 09 | 07 | Yd09d07 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 07
Y | d | d | 00 | 09 | 09 | Yd09d09 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 09
Y | d | d | 00 | 09 | 11 | Yd09d11 | First Y is reference W1: 00; First Y is reference W2: 09; First Y is reference W3: 11
Y | d | d | 00 | 11 | 01 | Yd11d01 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 01
Y | d | d | 00 | 11 | 03 | Yd11d03 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 03
Y | d | d | 00 | 11 | 05 | Yd11d05 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 05
Y | d | d | 00 | 11 | 07 | Yd11d07 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 07
Y | d | d | 00 | 11 | 09 | Yd11d09 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 09
Y | d | d | 00 | 11 | 11 | Yd11d11 | First Y is reference W1: 00; First Y is reference W2: 11; First Y is reference W3: 11
D | y | y | 00 | 01 | 01 | Dy01y01 | 11 | 00 | 00 | 0 | 1 | 1 | 11 | 0 | 0
D | y | y | 00 | 01 | 03 | Dy01y03 | 11 | 00 | 02 | 0 | 1 | 3 | 11 | 0 | 2
D | y | y | 00 | 01 | 05 | Dy01y05 | 11 | 00 | 04 | 0 | 1 | 5 | 11 | 0 | 4
D | y | y | 00 | 01 | 07 | Dy01y07 | 11 | 00 | 06 | 0 | 1 | 7 | 11 | 0 | 6
D | y | y | 00 | 01 | 09 | Dy01y09 | 11 | 00 | 08 | 0 | 1 | 9 | 11 | 0 | 8
D | y | y | 00 | 01 | 11 | Dy01y11 | 11 | 00 | 10 | 0 | 1 | 11 | 11 | 0 | 10
D | y | y | 00 | 03 | 01 | Dy03y01 | 09 | 00 | 10 | 0 | 3 | 1 | 9 | 0 | 10
D | y | y | 00 | 03 | 03 | Dy03y03 | 09 | 00 | 00 | 0 | 3 | 3 | 9 | 0 | 0
D | y | y | 00 | 03 | 05 | Dy03y05 | 09 | 00 | 02 | 0 | 3 | 5 | 9 | 0 | 2
D | y | y | 00 | 03 | 07 | Dy03y07 | 09 | 00 | 04 | 0 | 3 | 7 | 9 | 0 | 4
D | y | y | 00 | 03 | 09 | Dy03y09 | 09 | 00 | 06 | 0 | 3 | 9 | 9 | 0 | 6
D | y | y | 00 | 03 | 11 | Dy03y11 | 09 | 00 | 08 | 0 | 3 | 11 | 9 | 0 | 8
D | y | y | 00 | 05 | 01 | Dy05y01 | 07 | 00 | 08 | 0 | 5 | 1 | 7 | 0 | 8
D | y | y | 00 | 05 | 03 | Dy05y03 | 07 | 00 | 10 | 0 | 5 | 3 | 7 | 0 | 10
D | y | y | 00 | 05 | 05 | Dy05y05 | 07 | 00 | 00 | 0 | 5 | 5 | 7 | 0 | 0
D | y | y | 00 | 05 | 07 | Dy05y07 | 07 | 00 | 02 | 0 | 5 | 7 | 7 | 0 | 2
D | y | y | 00 | 05 | 09 | Dy05y09 | 07 | 00 | 04 | 0 | 5 | 9 | 7 | 0 | 4
D | y | y | 00 | 05 | 11 | Dy05y11 | 07 | 00 | 06 | 0 | 5 | 11 | 7 | 0 | 6
D | y | y | 00 | 07 | 01 | Dy07y01 | 05 | 00 | 06 | 0 | 7 | 1 | 5 | 0 | 6
D | y | y | 00 | 07 | 03 | Dy07y03 | 05 | 00 | 08 | 0 | 7 | 3 | 5 | 0 | 8
D | y | y | 00 | 07 | 05 | Dy07y05 | 05 | 00 | 10 | 0 | 7 | 5 | 5 | 0 | 10
D | y | y | 00 | 07 | 07 | Dy07y07 | 05 | 00 | 00 | 0 | 7 | 7 | 5 | 0 | 0
D | y | y | 00 | 07 | 09 | Dy07y09 | 05 | 00 | 02 | 0 | 7 | 9 | 5 | 0 | 2
D | y | y | 00 | 07 | 11 | Dy07y11 | 05 | 00 | 04 | 0 | 7 | 11 | 5 | 0 | 4
D | y | y | 00 | 09 | 01 | Dy09y01 | 03 | 00 | 04 | 0 | 9 | 1 | 3 | 0 | 4
D | y | y | 00 | 09 | 03 | Dy09y03 | 03 | 00 | 06 | 0 | 9 | 3 | 3 | 0 | 6
D | y | y | 00 | 09 | 05 | Dy09y05 | 03 | 00 | 08 | 0 | 9 | 5 | 3 | 0 | 8
D | y | y | 00 | 09 | 07 | Dy09y07 | 03 | 00 | 10 | 0 | 9 | 7 | 3 | 0 | 10
D | y | y | 00 | 09 | 09 | Dy09y09 | 03 | 00 | 00 | 0 | 9 | 9 | 3 | 0 | 0
D | y | y | 00 | 09 | 11 | Dy09y11 | 03 | 00 | 02 | 0 | 9 | 11 | 3 | 0 | 2
D | y | y | 00 | 11 | 01 | Dy11y01 | 01 | 00 | 02 | 0 | 11 | 1 | 1 | 0 | 2
D | y | y | 00 | 11 | 03 | Dy11y03 | 01 | 00 | 04 | 0 | 11 | 3 | 1 | 0 | 4
D | y | y | 00 | 11 | 05 | Dy11y05 | 01 | 00 | 06 | 0 | 11 | 5 | 1 | 0 | 6
D | y | y | 00 | 11 | 07 | Dy11y07 | 01 | 00 | 08 | 0 | 11 | 7 | 1 | 0 | 8
D | y | y | 00 | 11 | 09 | Dy11y09 | 01 | 00 | 10 | 0 | 11 | 9 | 1 | 0 | 10
D | y | y | 00 | 11 | 11 | Dy11y11 | 01 | 00 | 00 | 0 | 11 | 11 | 1 | 0 | 0
D | y | d | 00 | 01 | 00 | Dy01d00 | 11 | 00 | 11 | 0 | 1 | 0 | 11 | 0 | 11
D | y | d | 00 | 01 | 02 | Dy01d02 | 11 | 00 | 01 | 0 | 1 | 2 | 11 | 0 | 1
D | y | d | 00 | 01 | 04 | Dy01d04 | 11 | 00 | 03 | 0 | 1 | 4 | 11 | 0 | 3
D | y | d | 00 | 01 | 06 | Dy01d06 | 11 | 00 | 05 | 0 | 1 | 6 | 11 | 0 | 5
D | y | d | 00 | 01 | 08 | Dy01d08 | 11 | 00 | 07 | 0 | 1 | 8 | 11 | 0 | 7
D | y | d | 00 | 01 | 10 | Dy01d10 | 11 | 00 | 09 | 0 | 1 | 10 | 11 | 0 | 9
D | y | d | 00 | 03 | 00 | Dy03d00 | 09 | 00 | 09 | 0 | 3 | 0 | 9 | 0 | 9
D | y | d | 00 | 03 | 02 | Dy03d02 | 09 | 00 | 11 | 0 | 3 | 2 | 9 | 0 | 11
D | y | d | 00 | 03 | 04 | Dy03d04 | 09 | 00 | 01 | 0 | 3 | 4 | 9 | 0 | 1
D | y | d | 00 | 03 | 06 | Dy03d06 | 09 | 00 | 03 | 0 | 3 | 6 | 9 | 0 | 3
D | y | d | 00 | 03 | 08 | Dy03d08 | 09 | 00 | 05 | 0 | 3 | 8 | 9 | 0 | 5
D | y | d | 00 | 03 | 10 | Dy03d10 | 09 | 00 | 07 | 0 | 3 | 10 | 9 | 0 | 7
D | y | d | 00 | 05 | 00 | Dy05d00 | 07 | 00 | 07 | 0 | 5 | 0 | 7 | 0 | 7
D | y | d | 00 | 05 | 02 | Dy05d02 | 07 | 00 | 09 | 0 | 5 | 2 | 7 | 0 | 9
D | y | d | 00 | 05 | 04 | Dy05d04 | 07 | 00 | 11 | 0 | 5 | 4 | 7 | 0 | 11
D | y | d | 00 | 05 | 06 | Dy05d06 | 07 | 00 | 01 | 0 | 5 | 6 | 7 | 0 | 1
D | y | d | 00 | 05 | 08 | Dy05d08 | 07 | 00 | 03 | 0 | 5 | 8 | 7 | 0 | 3
D | y | d | 00 | 05 | 10 | Dy05d10 | 07 | 00 | 05 | 0 | 5 | 10 | 7 | 0 | 5
D | y | d | 00 | 07 | 00 | Dy07d00 | 05 | 00 | 05 | 0 | 7 | 0 | 5 | 0 | 5
D | y | d | 00 | 07 | 02 | Dy07d02 | 05 | 00 | 07 | 0 | 7 | 2 | 5 | 0 | 7
D | y | d | 00 | 07 | 04 | Dy07d04 | 05 | 00 | 09 | 0 | 7 | 4 | 5 | 0 | 9
D | y | d | 00 | 07 | 06 | Dy07d06 | 05 | 00 | 11 | 0 | 7 | 6 | 5 | 0 | 11
D | y | d | 00 | 07 | 08 | Dy07d08 | 05 | 00 | 01 | 0 | 7 | 8 | 5 | 0 | 1
D | y | d | 00 | 07 | 10 | Dy07d10 | 05 | 00 | 03 | 0 | 7 | 10 | 5 | 0 | 3
D | y | d | 00 | 09 | 00 | Dy09d00 | 03 | 00 | 03 | 0 | 9 | 0 | 3 | 0 | 3
D | y | d | 00 | 09 | 02 | Dy09d02 | 03 | 00 | 05 | 0 | 9 | 2 | 3 | 0 | 5
D | y | d | 00 | 09 | 04 | Dy09d04 | 03 | 00 | 05 | 0 | 9 | 4 | 3 | 0 | 7
D | y | d | 00 | 09 | 06 | Dy09d06 | 03 | 00 | 07 | 0 | 9 | 6 | 3 | 0 | 9
D | y | d | 00 | 09 | 08 | Dy09d08 | 03 | 00 | 09 | 0 | 9 | 8 | 3 | 0 | 11
D | y | d | 00 | 09 | 10 | Dy09d10 | 03 | 00 | 01 | 0 | 9 | 10 | 3 | 0 | 1
D | y | d | 00 | 11 | 00 | Dy11d00 | 01 | 00 | 01 | 0 | 11 | 0 | 1 | 0 | 1
D | y | d | 00 | 11 | 02 | Dy11d02 | 01 | 00 | 03 | 0 | 11 | 2 | 1 | 0 | 3
D | y | d | 00 | 11 | 04 | Dy11d04 | 01 | 00 | 03 | 0 | 11 | 4 | 1 | 0 | 5
D | y | d | 00 | 11 | 06 | Dy11d06 | 01 | 00 | 05 | 0 | 11 | 6 | 1 | 0 | 7
D | y | d | 00 | 11 | 08 | Dy11d08 | 01 | 00 | 05 | 0 | 11 | 8 | 1 | 0 | 9
D | y | d | 00 | 11 | 10 | Dy11d10 | 01 | 00 | 07 | 0 | 11 | 10 | 1 | 0 | 11
D | d | y | 00 | 00 | 01 | Dd00y01 | 11 | 11 | 09 | 0 | 0 | 1 | 11 | 11 | 0
D | d | y | 00 | 00 | 01 | Dd00y01 | 11 | 11 | 00 | 0 | 0 | 1 | 11 | 11 | 0
D | d | y | 00 | 00 | 03 | Dd00y03 | 09 | 09 | 00 | 0 | 0 | 3 | 9 | 9 | 0
D | d | y | 00 | 00 | 05 | Dd00y05 | 07 | 07 | 00 | 0 | 0 | 5 | 7 | 7 | 0
D | d | y | 00 | 00 | 07 | Dd00y07 | 05 | 05 | 00 | 0 | 0 | 7 | 5 | 5 | 0
D | d | y | 00 | 00 | 09 | Dd00y09 | 03 | 03 | 00 | 0 | 0 | 9 | 3 | 3 | 0
D | d | y | 00 | 00 | 11 | Dd00y11 | 01 | 01 | 00 | 0 | 0 | 11 | 1 | 1 | 0
D | d | y | 00 | 02 | 01 | Dd02y01 | 11 | 01 | 00 | 0 | 2 | 1 | 11 | 1 | 0
D | d | y | 00 | 02 | 03 | Dd02y03 | 09 | 11 | 00 | 0 | 2 | 3 | 9 | 11 | 0
D | d | y | 00 | 02 | 05 | Dd02y05 | 07 | 09 | 00 | 0 | 2 | 5 | 7 | 9 | 0
D | d | y | 00 | 02 | 07 | Dd02y07 | 05 | 07 | 00 | 0 | 2 | 7 | 5 | 7 | 0
D | d | y | 00 | 02 | 09 | Dd02y09 | 03 | 05 | 00 | 0 | 2 | 9 | 3 | 5 | 0
D | d | y | 00 | 02 | 11 | Dd02y11 | 01 | 03 | 00 | 0 | 2 | 11 | 1 | 3 | 0
D | d | y | 00 | 04 | 01 | Dd04y01 | 11 | 03 | 00 | 0 | 4 | 1 | 11 | 3 | 0
D | d | y | 00 | 04 | 03 | Dd04y03 | 09 | 01 | 00 | 0 | 4 | 3 | 9 | 1 | 0
D | d | y | 00 | 04 | 05 | Dd04y05 | 07 | 11 | 00 | 0 | 4 | 5 | 7 | 11 | 0
D | d | y | 00 | 04 | 07 | Dd04y07 | 05 | 09 | 00 | 0 | 4 | 7 | 5 | 9 | 0
D | d | y | 00 | 04 | 09 | Dd04y09 | 03 | 07 | 00 | 0 | 4 | 9 | 3 | 7 | 0
D | d | y | 00 | 04 | 11 | Dd04y11 | 01 | 05 | 00 | 0 | 4 | 11 | 1 | 5 | 0
D | d | y | 00 | 06 | 01 | Dd06y01 | 11 | 05 | 00 | 0 | 6 | 1 | 11 | 5 | 0
D | d | y | 00 | 06 | 03 | Dd06y03 | 09 | 03 | 00 | 0 | 6 | 3 | 9 | 3 | 0
D | d | y | 00 | 06 | 05 | Dd06y05 | 07 | 01 | 00 | 0 | 6 | 5 | 7 | 1 | 0
D | d | y | 00 | 06 | 07 | Dd06y07 | 05 | 11 | 00 | 0 | 6 | 7 | 5 | 11 | 0
D | d | y | 00 | 06 | 09 | Dd06y09 | 03 | 09 | 00 | 0 | 6 | 9 | 3 | 9 | 0
D | d | y | 00 | 06 | 11 | Dd06y11 | 01 | 07 | 00 | 0 | 6 | 11 | 1 | 7 | 0
D | d | y | 00 | 08 | 01 | Dd08y01 | 11 | 07 | 00 | 0 | 8 | 1 | 11 | 7 | 0
D | d | y | 00 | 08 | 03 | Dd08y03 | 09 | 05 | 00 | 0 | 8 | 3 | 9 | 5 | 0
D | d | y | 00 | 08 | 05 | Dd08y05 | 07 | 03 | 00 | 0 | 8 | 5 | 7 | 3 | 0
D | d | y | 00 | 08 | 07 | Dd08y07 | 05 | 01 | 00 | 0 | 8 | 7 | 5 | 1 | 0
D | d | y | 00 | 08 | 09 | Dd08y09 | 03 | 11 | 00 | 0 | 8 | 9 | 3 | 11 | 0
D | d | y | 00 | 08 | 11 | Dd08y11 | 01 | 09 | 00 | 0 | 8 | 11 | 1 | 9 | 0
D | d | y | 00 | 10 | 01 | Dd10y01 | 11 | 09 | 00 | 0 | 10 | 1 | 11 | 9 | 0
D | d | y | 00 | 10 | 03 | Dd10y03 | 09 | 07 | 00 | 0 | 10 | 3 | 9 | 7 | 0
D | d | y | 00 | 10 | 05 | Dd10y05 | 07 | 05 | 00 | 0 | 10 | 5 | 7 | 5 | 0
D | d | y | 00 | 10 | 07 | Dd10y07 | 05 | 03 | 00 | 0 | 10 | 7 | 5 | 3 | 0
D | d | y | 00 | 10 | 09 | Dd10y09 | 03 | 01 | 00 | 0 | 10 | 9 | 3 | 1 | 0
D | d | y | 00 | 10 | 11 | Dd10y11 | 01 | 11 | 00 | 0 | 10 | 11 | 1 | 11 | 0
D | d | d | 00 | 00 | 00 | Dd00d00 | 00 | 00 | 00 | 0 | 0 | 0
D | d | d | 00 | 00 | 02 | Dd00d02 | 00 | 00 | 02 | 0 | 0 | 2
D | d | d | 00 | 00 | 04 | Dd00d04 | 00 | 00 | 04 | 0 | 0 | 4
D | d | d | 00 | 00 | 06 | Dd00d06 | 00 | 00 | 06 | 0 | 0 | 6
D | d | d | 00 | 00 | 08 | Dd00d08 | 00 | 00 | 08 | 0 | 0 | 8
D | d | d | 00 | 00 | 10 | Dd00d10 | 00 | 00 | 10 | 0 | 0 | 10
D | d | d | 00 | 02 | 00 | Dd02d00 | 00 | 02 | 00 | 0 | 2 | 0
D | d | d | 00 | 02 | 02 | Dd02d02 | 00 | 02 | 02 | 0 | 2 | 2
D | d | d | 00 | 02 | 04 | Dd02d04 | 00 | 02 | 04 | 0 | 2 | 4
D | d | d | 00 | 02 | 06 | Dd02d06 | 00 | 02 | 06 | 0 | 2 | 6
D | d | d | 00 | 02 | 08 | Dd02d08 | 00 | 02 | 08 | 0 | 2 | 8
D | d | d | 00 | 02 | 10 | Dd02d10 | 00 | 02 | 10 | 0 | 2 | 10
D | d | d | 00 | 04 | 00 | Dd04d00 | 00 | 04 | 00 | 0 | 4 | 0
D | d | d | 00 | 04 | 02 | Dd04d02 | 00 | 04 | 02 | 0 | 4 | 2
D | d | d | 00 | 04 | 04 | Dd04d04 | 00 | 04 | 04 | 0 | 4 | 4
D | d | d | 00 | 04 | 06 | Dd04d06 | 00 | 04 | 06 | 0 | 4 | 6
D | d | d | 00 | 04 | 08 | Dd04d08 | 00 | 04 | 08 | 0 | 4 | 8
D | d | d | 00 | 04 | 10 | Dd04d10 | 00 | 04 | 10 | 0 | 4 | 10
D | d | d | 00 | 06 | 00 | Dd06d00 | 00 | 06 | 00 | 0 | 6 | 0
D | d | d | 00 | 06 | 02 | Dd06d02 | 00 | 06 | 02 | 0 | 6 | 2
D | d | d | 00 | 06 | 04 | Dd06d04 | 00 | 06 | 04 | 0 | 6 | 4
D | d | d | 00 | 06 | 06 | Dd06d06 | 00 | 06 | 06 | 0 | 6 | 6
D | d | d | 00 | 06 | 08 | Dd06d08 | 00 | 06 | 08 | 0 | 6 | 8
D | d | d | 00 | 06 | 10 | Dd06d10 | 00 | 06 | 10 | 0 | 6 | 10
D | d | d | 00 | 08 | 00 | Dd08d00 | 00 | 08 | 00 | 0 | 8 | 0
D | d | d | 00 | 08 | 02 | Dd08d02 | 00 | 08 | 02 | 0 | 8 | 2
D | d | d | 00 | 08 | 04 | Dd08d04 | 00 | 08 | 04 | 0 | 8 | 4
D | d | d | 00 | 08 | 06 | Dd08d06 | 00 | 08 | 06 | 0 | 8 | 6
D | d | d | 00 | 08 | 08 | Dd08d08 | 00 | 08 | 08 | 0 | 8 | 8
D | d | d | 00 | 08 | 10 | Dd08d10 | 00 | 08 | 10 | 0 | 8 | 10
D | d | d | 00 | 10 | 00 | Dd10d00 | 00 | 10 | 00 | 0 | 10 | 0
D | d | d | 00 | 10 | 02 | Dd10d02 | 00 | 10 | 02 | 0 | 10 | 2
D | d | d | 00 | 10 | 04 | Dd10d04 | 00 | 10 | 04 | 0 | 10 | 4
D | d | d | 00 | 10 | 06 | Dd10d06 | 00 | 10 | 06 | 0 | 10 | 6
D | d | d | 00 | 10 | 08 | Dd10d08 | 00 | 10 | 08 | 0 | 10 | 8
D | d | d | 00 | 10 | 10 | Dd10d10 | 00 | 10 | 10 | 0 | 10 | 10
ON
OFF

## Diff Characteristics
Stability test 3-phase for RET 670 | [15 empty] | ABB
I diff | 40 | 0.21869 | [6 empty] | Values for points when using Omicron diff characteristics
End Sec 1 | 1.5 | 0.8201 | times of Wdg. 1 rated current | [5 empty] | Idiff | 0.4 | 0.4 | 0.4
End Sec 2 | 4 | 2.1869 | times of Wdg. 1 rated current | [5 empty] | Ibias | 0.6 | 1.5 | 4
Slope 1 | 30 | [11 empty] | NEW RAFHA PP S/S DATE : 01/07/2012
Slope 2 | 80 | [8 empty] | FINAL TEST |  |  | CIRCUIT No : UAT3
I base W1 | 0.54673
I base W2 | 0.87477
I base W3 | #DIV/0!
Slope 1 % |  | Slope 2 % |  | Ibias 1st cross | Idiff | Ibias 2nd cross | Idiff 2nd cross
40 |  | 80 |  | 1.5 | 0.4 | 4 | 1.15
Bias Points to be Tested [pu] | W1 Start Current [A_Sec.] |  | W2 Start Current [A_Sec.] | W3 Start Current [A_Sec.] | Zone 1 | Zone 2 | Zone 3 | Diff Current PU | Diff Current for the given Bias values | Expected W2 Trip Current [A_Sec.] | Expected W3 Trip Current [A_Sec.] | Measured W2 Current at Trip [A_Sec.] | Measured W3 Current at Trip [A_Sec.] | Actual Diff Current at Trip W1-W2 | Actual Diff Current at Trip W1-W3 | Diff Current Error in [%] W1-W2 | Diff Current Error in [%] W1-W2
0.4 | 0.21869 |  | 0 | 0 | 0.21869 | 0.038271 | -0.94585 | 0.4 | 0.21869 | 0 | #DIV/0! | 0 |  | 0.21869 |  | 0%
0.6 | 0.32804 |  | 0.52486 | #DIV/0! | 0.21869 | 0.071075 | -0.85837 | 0.4 | 0.21869 | 0.17495 | #DIV/0! | 0.082 |  | 0.27679 |  | -5.81%
1 | 0.54673 |  | 0.87477 | #DIV/0! | 0.21869 | 0.13668 | -0.68342 | 0.4 | 0.21869 | 0.52486 | #DIV/0! | 0.37 |  | 0.31548 |  | -9.679%
1.5 | 0.8201 |  | 1.3122 | #DIV/0! | 0.21869 | 0.21869 | -0.46472 | 0.4 | 0.21869 | 0.96225 | #DIV/0! | 0.491 |  | 0.51322 |  | -29.45%
1.5 | 0.8201 |  | 1.3122 | #DIV/0! | 0.21869 | 0.21869 | -0.46472 | 0.4 | 0.21869 | 0.96225 | #DIV/0! | 0.564 |  | 0.4676 |  | -24.89%
1.75 | 0.95678 |  | 1.5309 | #DIV/0! | 0.21869 | 0.2597 | -0.35538 | 0.475 | 0.2597 | 1.1153 | #DIV/0! | 0.646 |  | 0.55303 |  | -29.33%
2 | 1.0935 |  | 1.7495 | #DIV/0! | 0.21869 | 0.3007 | -0.24603 | 0.55 | 0.3007 | 1.2684 | #DIV/0! | 0.707 |  | 0.65159 |  | -35.09%
2.25 | 1.2301 |  | 1.9682 | #DIV/0! | 0.21869 | 0.34171 | -0.13668 | 0.625 | 0.34171 | 1.4215 | #DIV/0! | 0.785 |  | 0.73952 |  | -39.78%
2.5 | 1.3668 |  | 2.1869 | #DIV/0! | 0.21869 | 0.38271 | -0.027337 | 0.7 | 0.38271 | 1.5746 | #DIV/0! | 0.859 |  | 0.82996 |  | -44.72%
4 | 2.1869 |  | 3.4991 | #DIV/0! | 0.21869 | 0.62874 | 0.62874 | 1.15 | 0.62874 | 2.4931 | #DIV/0! | 1 |  | 1.5619 |  | -93.32%
3.5 | 1.9136 |  | 3.0617 | #DIV/0! | 0.21869 | 0.54673 | 0.41005 | 1 | 0.54673 | 2.1869 | #DIV/0! | 1.05 |  | 1.2573 |  | -71.06%
4 | 2.1869 |  | 3.4991 | #DIV/0! | 0.21869 | 0.62874 | 0.62874 | 1.15 | 0.62874 | 2.4931 | #DIV/0! | 1.099 |  | 1.5001 |  | -87.13%
4.5 | 2.4603 |  | 3.9365 | #DIV/0! | 0.21869 | 0.71075 | 0.84744 | 1.55 | 0.84744 | 2.5806 | #DIV/0! | 1.142 |  | 1.7465 |  | -89.91%
5 | 2.7337 |  | 4.3739 | #DIV/0! | 0.21869 | 0.79276 | 1.0661 | 1.95 | 1.0661 | 2.6681 | #DIV/0! | 1.193 |  | 1.988 |  | -92.19%
5.5 | 3.007 |  | 4.8113 | #DIV/0! | 0.21869 | 0.87477 | 1.2848 | 2.35 | 1.2848 | 2.7555 | #DIV/0! | 1.246 |  | 2.2283 |  | -94.35%
6 | 3.2804 |  | 5.2486 | #DIV/0! | 0.21869 | 0.95678 | 1.5035 | 2.75 | 1.5035 | 2.843 | #DIV/0! | 1.291 |  | 2.4735 |  | -97%
| Constant Current |  | Ramp Down from this value | [6 empty] | to less than this value | [5 empty] | Accuracy +/- 2% of Ir
ENTER YOUR VALUES IN CELLS MARKED WITH THIS YELLOW COLOR