## Sheet1
SETTING CALCULATION FOR RED&REL 670 RELAYS
| CT PRIM | 1200 | VT PRIM | 132000 | CTR/VTR | 1.0455
| CT SEC | 1 | VT SEC | 115
| CTR | 1200 | VTR | 1147.8261
| SETTING PARAMETERS |  |  | SECONDARY EXPECTED VALUES ACCORDING TO THE CHARACTARISTIC
| Z1 | RFPE | 30 | R-N | 31.3636 | R1 | 0.44
|  | RFPP | 17.5 | X-N | 16.3021 | R0 | 5.37
|  | X1 | 8.75 | R P-P | 9.1477 | Ø(PH-E) | 82.357
|  | XO | 29.28 | XP-P | 9.1477 | Ø(PH-PH) | 87.0862
| SETTING PARAMETERS |  |  | SECONDARY EXPECTED VALUES ACCORDING TO THE CHARACTARISTIC
| Z2 | RFPE | 36 | R-N | 37.6364 | R1 | 1.29
|  | RFPP | 47.1 | X-N | 43.1215 | R0 | 15.75
|  | X1 | 23.55 | R P-P | 24.6205 | Ø(PH-E) | 81.541
|  | XO | 76.64 | XP-P | 24.6205 | Ø(PH-PH) | 86.8297
| SETTING PARAMETERS |  |  | SECONDARY EXPECTED VALUES ACCORDING TO THE CHARACTARISTIC
| Z3 | RFPE | 43.2 | R-N | 45.1636 | R1 | 2.84
|  | RFPP | 56.52 | X-N | 103.615 | R0 | 35.25
|  | X1 | 54.59 | R P-P | 29.5445 | Ø(PH-E) | 82.129
|  | XO | 188.15 | XP-P | 57.0714 | Ø(PH-PH) | 86.9869
| SETTING PARAMETERS |  |  | SECONDARY EXPECTED VALUES ACCORDING TO THE CHARACTARISTIC
| Z4 | RFPE | 43.2 | R-N | 45.1636 | R1 | 2.84
|  | RFPP | 56.52 | X-N | 103.615 | R0 | 35.25
|  | X1 | 54.59 | R P-P | 29.5445 | Ø(PH-E) | 82.129
|  | XO | 188.15 | XP-P | 57.0714 | Ø(PH-PH) | 86.9869
| SETTING PARAMETERS |  |  | SECONDARY EXPECTED VALUES ACCORDING TO THE CHARACTARISTIC
| Z5 | RFPE | 0 | R-N | 0 | R1 | 1
|  | RFPP | 0 | X-N | 0 | R0 | 1
|  | X1 | 0 | R P-P | 0 | Ø(PH-E) | 0
|  | XO | 0 | XP-P | 0 | Ø(PH-PH) | 0
PHASE SELECTION
| PHS |  |  |  | PH-E | PH-PH | 3-PH
|  | RFRVPE | 43.2 | RFw | 45.1636 | 29.5445 | 39.3927
|  | RFRvPP | 56.52 | XFw | 62.093 | 35.4514 | 47.2685
|  | X1 | 33.91 | RRv | 45.1636 | 29.5445 | 39.3927
|  | XO | 110.36 | XRv | 62.093 | 35.4514 | 47.2685
|  | RFFwPE | 43.2
|  | RFFwPP | 56.52
POWER SWING CALCULATION
| PSD | R1FINFW | 62.17 | RInFw | 64.9959 | F(FW) | 17.375
|  | R1FINRv | 62.17 | RInRv | 64.9959 | F(Rv) | 17.375
|  | X1FINFW | 60 | XInFw | 62.7273 | AT OPERATION OF LdCh=ON
|  | X1FINRv | 60 | XInRv | 62.7273 | ROutFw | 72.6591
|  | KLDRFW | 0.75 | ROutFw | 83.1607 | RInFw | 54.4943
|  | KLDRRv | 0.75 | ROutRv | 83.1607 | ROutRv | 72.6591
|  | RLdOutFw | 69.5 | XOutFw | 80.892 | RInRv | 54.4943
|  | RLdOutRv | 69.5 | XOutRv | 80.892
PSD CALCULATION AT RLdOutFw=RLdOutRv
F: DIFFRANCE BETWEEN INNER &OUTER ZONES
FAULT LOCATOR
| FLO | X1L | 0.57134 | zL(ph-e)sec | 0.4673 | FOR 1-PH FAULTS
|  | X0L | 0.19826 | zL(ph-ph)sec | 0.59731 | FOR 3-PH &2-PH FAULTS
|  | R1L | 0.041469 | XL(M)sec | 0.069091 | FOR 1- PH FAULTS WITH MUTUAL
|  | R0L | 0.18469 | ZΦ | 78.7131 | TEST ANGLE FOR 1-PH
|  | X0M | 0 | ZΦ | 85.8487 | TEST ANGLE FOR 2-PH
|  | LINE LENGTH | 2.3 | P(1-PH) | 45.4783 | FAULT LENGTH
|  | Zx inj 1-ph | 9.24 | P(PH-PH) | 0
|  | Zx inj ph-ph | 0 | P(1-PH)MUTUAL | 0
|  | Zx inj-mutual | 0
INJECT HEALTHY CONDITION MORE THAN 2 SEC THEN APPLY FAULT CONDITION WITH IZxI AND ZΦ
P= THE EXPECTED FAULT DISTANCE
DIFFRENTIAL PROTECTION
| L3D | Idmin | 0.2 | Id section 1 | 0.2
|  | End Section1 | 1.25 | Id section 2 | 0.34
|  | End Section2 | 3 | Id section 3 | 1.7
|  | Slop Section2 | 0.4
|  | Slop Section3 | 0.8
|  | Ibase | 1
|  | IBias section1 | 1.1
|  | IBias section2 | 1.6
|  | IBias section3 | 4
| Section 1 |  | 0 ≤ IBias ≤ End Section1*IBase
| Slop section 2 |  | Endsection1*IBase ≤ IBias ≤ Endsection2*IBase
| Slop section 3 |  | IBias ≥ End section2*IBase
| TOC | IEC CURVE TYPE |  | CONSTANTS
|  |  |  | A | P | TIME (sec)
|  | NORMAL INVERSE |  | 0.14 | 0.02 | 6.3019
|  | VERY INVERSE |  | 13.5 | 1 | 6.75
|  | INVERSE |  | 0.14 | 0.02 | 6.3019
|  | EXTREMLY INVERSE |  | 80 | 2 | 10
|  | SHORT TIME INVERSE |  | 0.05 | 0.04 | 1.113
|  | LONG TIME INVERSE |  | 120 | 1 | 60
|  | K1(TMS) set |  | 1
|  | I1> (set) |  | 1
|  | I(inj) |  | 3
|  | I(inj)/I1> (set) |  | 3
TOC: TIME OVER CURRENT
PREPARED BY
ENG/ EHAB SHAWKAT
AT&C